## Panel L
Panel R2
Voltage: 120/208V 3ph 4W |  |  |  |  | Cabinet: Nema 3R Surface Mount
Mains: 200A Main Breaker 16KAIC |  |  |  |  | Type:Panel Board
Device |  |  | Branch Circuit | Space |  | Branch Circuit | Device
Amps | Poles | Notes |  |  |  |  | Notes | Poles | Amps
60 | 3 |  | 15Door CU#3/Defrost Ckt | 1 | 2 | 15 Door Lights |  | 1 | 20
| - |  | " | 3 | 4 | 15 Door Fans/Anti sweats |  | 1 | 20
| - |  | " | 5 | 6 | 15 Door Fans/Anti sweats |  | 1 | 20
50 | 3 |  | 2,3,4 Door Coolers | 7 | 8 | 15 Door Fans/Anti sweats |  | 1 | 20
| - |  | CU #1/Defrost Ckt | 9 | 10 | 2 Door Fans/Anti sweats/lights |  | 1 | 20
| - |  | " | 11 | 12 | 3 Door Fans/Anti sweats/lights |  | 1 | 20
20 | 3 |  | 8' Sandwich Merchandiser CU #2 | 13 | 14 | 4 Door Fans/Anti sweats/lights |  | 1 | 20
| - |  | " | 15 | 16 | 8' Sandwich cooler |  | 1 | 20
| - |  | " | 17 | 18 | 12' Produce Merchandiser CU |  | 1 | 30
30 | 3 |  | Spare | 19 | 20 | - |  | 1
|  |  |  | 21 | 22 | - |  | 1
|  |  |  | 23 | 24 | Spare |  | 1 | 20
20 | 1 |  | Spare | 25 | 26 | Spare |  | 1 | 20
20 | 1 |  | Spare | 27 | 28 | Spare |  | 1 | 20
20 | 1 |  | Spare | 29 | 30 | Spare |  | 1 | 20
20 | 1 |  | Spare | 31 | 32 | Spare |  | 1 | 20
| 1 |  | Space | 33 | 34 | Space |  | 1
| 1 |  | Space | 35 | 36 | Space |  | 1
| 1 |  | Space | 37 | 38 | Space |  | 1
| 1 |  | Space | 39 | 40 | Space |  | 1
| 1 |  | Space | 41 | 42 | Space |  | 1